## FIREPRO
RUNEHA INC.
Block 7 Lot 9 Trails of Maia Alta, Brgy. Dalig, Antipolo City
Project: | DESIGN AND BUILD OF FIRE PROTECTION SYSTEM
Location: | 66.5 MLD SEAWATER DESALINATION FACILITY at Brgy. Ingore, La Paz, Iloilo
Client: | J.E. MANALO & CO., INC. |  |  |  |  | Estimated by: |  | NCV
Subject: | BILL OF QUANTITES (BOQ) - DESIGN AND BUILD OF FIRE PROTECTION SYSTEM | [5 empty] | Date: | 2024-10-30
COST BREAKDOWN
ITEM | DESCRIPTION | QTY | UNIT | MATERIAL COST |  | LABOR COST |  | AMOUNT
|  |  |  | UNIT COST | AMOUNT | UNIT COST | AMOUNT
A | GENERAL REQUIREMENTS
1 | Mobilization / Demobilization | 2 | lot | 90000 | 180000 | 50000 | 100000 | 280000
2 | Permits/Clearances | 2 | lot | by Client |  |  |  | 0
3 | Power & Water Consumption | 2 | lot | 40000 | 80000 | 50000 | 100000 | 180000
4 | Bonds & Insurances | 2 | lot | 80000 | 160000 | 50000 | 100000 | 260000
5 | Site Expenses, Accomodation & Temfacil | 2 | lot | 130000 | 260000 | 100000 | 200000 | 460000
6 | Health & Safety Requirement & PPE's | 2 | lot | 40000 | 80000 | 50000 | 100000 | 180000
7 | Waste & Debris Disposal | 2 | lot | 30000 | 60000 | 25000 | 50000 | 110000
8 | Equipment Shiffing Fee, Hauling and Handling of Materials | 2 | lot | 110000 | 220000 | 100000 | 200000 | 420000
9 | Scaffoldings & Platforms | 2 | lot | 30000 | 60000 | 25000 | 50000 | 110000
10 | Site Supervision & Management | 2 | lot | 350000 | 700000 | 200000 | 400000 | 1100000
11 | MVAC Design Calculation, Drafting & Coordination Fee | 2 | lot | 150000 | 300000 | 100000 | 200000 | 500000
12 | As-Built Drawings & Other Documents | 2 | lot | 15000 | 30000 | 20000 | 40000 | 70000
| General Requirements - Subtotal | [6 empty] | 3670000
B | FIRE PROTECTION WORKS
1 | Fire Pump No. 1 (UL/FM) - DIESEL
| Vertical Turbine Diesel Engine Fire Pump, 750GPM, 100PSI, 125HP, 220V complete with Fire Pump Controller & Accessories such as Fuel Tank 130 Gallons. | 2 | no/s | 4500000 | 9000000 | 50000 | 50000 | 9050000
2 | Fire Pump No. 2 (UL/FM) - ELECTRIC
| Vertical Turbine Motor Driven Fire Pump, 750GPM, 100PSI, 125HP, 380-400V/3PH/60HZ complete with Fire Pump Controller & Accessories. | 2 | no/s | 3100000 | 6200000 | 50000 | 50000 | 6250000
3 | Jockey Pump
| Vertical In-Line JockeyPump, 30GPM, 110PSI, 5HP, 380V/3HP/60HZ complete with Jockey Pump Controller & Accessories. | 3 | no/s | 310000 | 930000 | 20000 | 20000 | 950000
| Pump Mounting Accessories | 3 | lot | 20000 | 60000 | 15000 | 15000 | 75000
| Control Wiring (Only from Fire Pump Panel to Pump) | 3 | lot | 170000 | 510000 | 100000 | 100000 | 610000
| Testing / Commissioning | 3 | lot | 75000 | 225000 | 50000 | 50000 | 275000
4 | B.I Pipes, Sched. 40 (Pump Room)
| ø150mm | 35 | m | 3000 | 105000 | 2500 | 87500 | 192500
| ø100mm | 15 | m | 2000 | 30000 | 2000 | 30000 | 60000
| ø50mm | 8 | m | 500 | 4000 | 500 | 4000 | 8000
5 | B.I Fittings (MECH)
Elbow 90
| ø150mm | 20 | no/s | 1550 | 31000 | 800 | 16000 | 47000
| ø100mm | 3 | no/s | 1550 | 4650 | 700 | 2100 | 6750
| ø50mm | 3 | no/s | 600 | 1800 | 400 | 1200 | 3000
Equal Tee
| ø150mm | 15 | no/s | 3000 | 45000 | 800 | 12000 | 57000
Reducer
| ø100mm x ø150mm | 3 | no/s | 2500 | 7500 | 800 | 2400 | 9900
| ø32mm x ø50mm | 3 | no/s | 600 | 1800 | 400 | 1200 | 3000
6 | UNDERGROUND PIPES (LOOP PIPING)
HDPE PIPE
| ø150mm | 800 | m | 2000 | 1600000 | 1000 | 800000 | 2400000
| ø100mm | 500 | m | 1000 | 500000 | 500 | 250000 | 750000
| ø65mm | 70 | m | 500 | 35000 | 350 | 24500 | 59500
Elbow 90
| ø150mm | 15 | no/s | 3000 | 45000 | 700 | 10500 | 55500
| ø100mm | 22 | no/s | 1000 | 22000 | 600 | 13200 | 35200
| ø65mm | 55 | no/s | 500 | 27500 | 350 | 19250 | 46750
Elbow 45
| ø150mm | 12 | no/s | 2000 | 24000 | 700 | 8400 | 32400
| ø100mm | 15 | no/s | 1000 | 15000 | 600 | 9000 | 24000
| ø65mm | 13 | no/s | 450 | 5850 | 350 | 4550 | 10400
Tee Reducer
| ø150mm x ø100mm | 35 | no/s | 4000 | 140000 | 700 | 24500 | 164500
| ø100mm x ø65mm | 28 | no/s | 1500 | 42000 | 600 | 16800 | 58800
| HDPE Flange, ø65mm | 35 | no/s |  | 0 | 352 | 12320 | 12320
| B.I Flange, ø40mm | 25 | no/s |  | 0 | 353 | 8825 | 8825
7 | B.I Pipes, Sched. 40 (Admin Building)
| ø100mm | 125 | m | 1600 | 200000 | 2000 | 250000 | 450000
| ø65mm | 25 | m | 1000 | 25000 | 600 | 15000 | 40000
| ø50mm | 30 | m | 600 | 18000 | 500 | 15000 | 33000
| ø40mm | 105 | m | 400 | 42000 | 400 | 42000 | 84000
| ø32mm | 115 | m | 350 | 40250 | 300 | 34500 | 74750
| ø25mm | 220 | m | 500 | 110000 | 250 | 55000 | 165000
8 | B.I Fittings (MECH)
| B.I Fittings | 3 | lot | 400000 | 1200000 | 250000 | 750000 | 1950000
9 | Sprinkler Heads
| Pendent Sprinkler Heads (Viking) | 400 | no/s | 500 | 200000 | 250 | 100000 | 300000
10 | Valves & Accessories
(Fire & Jockey Pump)
OS&Y Gate Valve
| 150mmØ | 10 | no/s | 39400 | 394000 | 5000 | 50000 | 444000
Gate Valve
| 100mmØ | 3 | no/s | 15000 | 45000 | 3000 | 9000 | 54000
| 50mmØ | 3 | no/s | 5000 | 15000 | 700 | 2100 | 17100
Check Valve
| 150mmØ | 3 | no/s | 35000 | 105000 | 5000 | 15000 | 120000
| 50mmØ | 2 | no/s | 6000 | 12000 | 700 | 1400 | 13400
Alarm Check Valve
| 150mmØ | 3 | no/s | 90000 | 270000 | 6000 | 18000 | 288000
Wye Strainer
| 50mmØ | 3 | no/s | 6000 | 18000 | 700 | 2100 | 20100
Water Flow Meter
| 150mmØ | 3 | no/s | INCLUDED IN FP |  | 5000 | 15000 | 15000
Pressure Reducing Valve
| 150mmØ | 3 | no/s | INCLUDED IN FP |  | 5000 | 15000 | 15000
Air Release Valve
| 40mmØ | 3 | no/s | INCLUDED IN FP |  | 2000 | 6000 | 6000
Waste Cone
| 150mmØ | 3 | no/s | INCLUDED IN FP |  | 5000 | 15000 | 15000
Mechanical Flexible Coupling
| 150mmØ | 5 | no/s | 1750 | 8750 | 1500 | 7500 | 16250
| 50mmØ | 3 | no/s | 1250 | 3750 | 1000 | 3000 | 6750
Essentric Reducer
| Supervisory Switch | 3 | no/s | 9000 | 27000 | 2000 | 6000 | 33000
| Pressure Gauge | 15 | no/s | 2500 | 37500 | 300 | 4500 | 42000
| Sensing Line Assembly | 3 | set/s | 11000 | 33000 | 10000 | 30000 | 63000
| Sight Glass | 3 | no/s | 4000 | 12000 | 1000 | 3000 | 15000
| Neoprene Non-Skid Rubber Isolator, 6" x 6" x 3/4" thk. | 10 | no/s | 500 | 5000 | 400 | 4000 | 9000
| Slip-On Flange, 200mmØ | 5 | no/s | 2000 | 10000 | 1500 | 7500 | 17500
| Slip-On Flange, 150mmØ | 50 | no/s | 1000 | 50000 | 1200 | 60000 | 110000
| Slip-On Flange, 100mmØ | 20 | no/s | 950 | 19000 | 1000 | 20000 | 39000
| Blind Flange, 150mmØ | 4 | no/s | 1650 | 6600 | 1200 | 4800 | 11400
| High Tensile Bolt & Nut with Washer, 3/4"Ø x 3" (L) | 400 | no/s | 90 | 36000 | 35 | 14000 | 50000
| Rigid Plate pipe support with anchor bolt on concerete pad | 2 | lot | 2250 | 4500 | 3000 | 6000 | 10500
11 | Floor Control Valve
Supervisory Valve
| 100mmØ | 3 | no/s | 39000 | 117000 | 5000 | 15000 | 132000
Water Flow Detector
| 100mmØ | 3 | no/s | 17000 | 51000 | 4000 | 12000 | 63000
Check Valve
| 100mmØ | 3 | no/s | 32000 | 96000 | 5000 | 15000 | 111000
| Supervisory Switch | 3 | no/s | 9000 | 27000 | 2000 | 6000 | 33000
| Pressure Gauge | 3 | no/s | 2500 | 7500 | 300 | 900 | 8400
| Slip-On Flange, 150mmØ | 9 | no/s | 1000 | 9000 | 1200 | 10800 | 19800
| High Tensile Bolt & Nut with Washer, 3/4"Ø x 3" (L) | 65 | no/s | 90 | 5850 | 35 | 2275 | 8125
12 | Auxillary Drain Assembly
| Sight Glass, 25mmØ | 1 | no/s | 1300 | 1300 | 500 | 500 | 1800
| Inspector Test Valve, 25mmØ | 1 | no/s | 4000 | 4000 | 500 | 500 | 4500
| Ball Valve, 25mmØ | 1 | no/s | 4000 | 4000 | 500 | 500 | 4500
| B.I Union Patente, 25mmØ | 3 | no/s | 700 | 2100 | 500 | 1500 | 3600
13 | Main Pipe Risers
| FDC with Cap & Chain, 150x65x65x65 | 3 | no/s | 45000 | 135000 | 5000 | 15000 | 150000
| Check Valve, 150Ø | 3 | no/s | 32000 | 96000 | 5000 | 15000 | 111000
| Pump Test, 150x65x65x65 | 3 | no/s | 12000 | 36000 | 4000 | 12000 | 48000
| Fire Hose Valve with Cap & Chain, 65mmØ | 3 | no/s | 8000 | 24000 | 2500 | 7500 | 31500
| Slip-On Flange, 150mmØ | 12 | no/s | 550 | 6600 | 1200 | 14400 | 21000
| High Tensile Bolt & Nut with Washer, 3/4"Ø x 3" (L) | 22 | no/s | 50 | 1100 | 35 | 770 | 1870
14 | Inspector Test Connection
| Sight Glass, 25mmØ | 3 | no/s | 1500 | 4500 | 500 | 1500 | 6000
| Ball Valve, 25Ø | 3 | no/s | 3000 | 9000 | 500 | 1500 | 10500
15 | Fire Hose Cabinet
| - made of Ga.# 18 galvanized iron steel painted (interior and exterior body) with one coat of red lead primer before painting with 2 coat of fire engine red color | 15 | set/s | 30000 | 450000 | 5000 | 75000 | 525000
- 1/8" thk. Clear Glass
- 30m x 40Ø fire hose, double jacketed
- 40Ø angle valve, FHV, UL/FM
- 40Ø adjustable pistol type (tight grip nozzle)
- Semi-automatic hose rack
- Piano Hinge
- Brass nipple, adaptor and coupling
- 9 lbs. Fire Extinguisher, dry chemical, class ABC
16 | Fire Hose Cabinet & Hydrant | 35 | set/s | 80000 | 2800000 | 6500 | 227500 | 3027500
17 | Portable Fire Extinguisher
| - 10 lbs. FE Dry Chemical, class ABC | 35 | set/s | 1500 | 52500 | 500 | 17500 | 70000
18 | FIRE SUPPRESSION SYSTEM (EE ROOM)
| FM 200 | 3 | lot | 1450000 | 4350000 | 200000 | 600000 | 4950000
| B. Fire Protection Works - Subtotal | [6 empty] | 35125190
C | OTHER ITEMS
1 | Builders Work & Excavation | 3 | lot | 400000 | 1200000 | 200000 | 600000 | 1800000
2 | Wall Chipping, Pipe Sleeving, Grouting & Sealing | 3 | lot | 20000 | 60000 | 25000 | 75000 | 135000
3 | Pipe Supports & Hangers | 3 | lot | 100000 | 300000 | 100000 | 300000 | 600000
4 | Painting Works | 3 | lot | 20000 | 60000 | 20000 | 60000 | 120000
5 | Hydro Test | 3 | lot | 15000 | 45000 | 40000 | 120000 | 165000
6 | Miscellaneous & Consumables | 3 | lot | 300000 | 900000 | 150000 | 450000 | 1350000
| C. Other Items - Subtotal | [6 empty] | 4170000
| SUB-TOTAL OF ITEM A TO C | [6 empty] | 42965190
| Plus 12% VAT | [6 empty] | 5155822.8
| GRAND TOTAL | [6 empty] | 48121012.8